## Table 1
Insert Facility Name
Preventive Maintenance Work Plan
Frequency Key
W – Weekly M - Monthly Q - Quarterly SA- Semi-Annually A- Annually SST - Seasonal Start-Up SSH - Season Shut Down
Fans (Supply, Exhaust, Return)(Belt or Shaft Driven)
Critical Tasks | Frequency | Status | Date Completed | Initials
Inspect unit for unusual noise and/or vibration, ensure that it is in good working order. | Q
If unit is not running or an identified problem requires the unit to be serviced, perform ALL Non- Critical Tasks listed below. | Q
If present, inspect belts for proper tension and wear (if belts are replaced, record belt type and replacement date on unit) | Q
Inspect fan and motor assemble for proper alignment.
Provide lubrication, if necessary. | Q
Clean entire unit, motor and fan assembly with a damp cloth. | Q
Check exhaust fan intake grills for dirt/debris. | Q
Other recommended tasks
For fans 2HP or more, check load amps. | A
Inspect fan and motor pulleys for proper alignment. | A
Inspect fan blades and moving parts for excessive wear. | A
Inspect all fan wiring for deterioration. | A
Ensure tightness of all electrical connections. | A
Inspect motor starter/control center. | A
Ensure that overload settings are proper | A
Verify correct operation of starter. | A
Inspect electrical contact surfaces. | A
Inspect fan assembly. | A
Verify tightness of balance weights. | A
Preventive Maintenance Work Plan
Frequency Key
W – Weekly M - Monthly Q - Quarterly SA- Semi-Annually A- Annually SST - Seasonal Start-Up SSH - Season Shut Down
Variable Air Volume Terminal Units
Critical Tasks | Frequency | Status | Date Completed | Initials
Observe unit, note any unusual noise and/or vibrations. | SA
Ensure that unit is supplying air if in demand, vice versa. | SA
Provide lubrication, if necessary. | SA
Other recommended tasks
Inspect all pneumatic/electrical connections, tighten if necessary. | SA
Observe and inspect VAV control box. | SA
Inspect all fan wiring for deterioration. | SA
Inspect motor-shaft connection and ensure tightness. | SA
Clean dampers and fan blades. | SA
Inspect controls and cycle actuators to ensure proper operation. | SA
Verify that dampers open and close fully. | SA
Inspect all linkages and ensure proper positioning. | SA
Preventive Maintenance Work Plan
Frequency Key
W – Weekly M - Monthly Q - Quarterly SA- Semi-Annually A- Annually SST - Seasonal Start-Up SSH - Season Shut Down
Heating and Ventilation Units
Critical Tasks, to be performed monthly | Frequency | Status | Date Completed | Initials
Inspect entire unit for unusual noise and/or vibration, ensure that it is in good working | M
order.
Provide lubrication, if necessary | M
Check that damper linkages are properly connected and operating | M
Inspect piping and fittings for leaks (steam, condensate, hot water, chilled water). | M
Inspect ductwork flexible connectors for abnormalities or leaks. | M
Inspect felt/rubber gaskets around access doors. | M
Following inspection, record observations and deficiencies, if any. | M
Check outside air intake louvers. | M
If problems are identified and unit requires servicing, perform all Non-Critical Tasks for the problematic components. | M
Inspect pre and final filters for abnormal accumulation of dirt and debris, replace if necessary. Write installation date on new filters. | Q
Clean filter rack and vacuum filter section after removal of old filters and prior to installing new filters. | Q
Inspect filter rack and ensure that air path does not bypass filters. | Q
Inspect coils (steam, hot water, chilled water) for accumulation of dirt and debris, clean if necessary. | Q
Inspect/adjust humidifier, if present | Q
Check access doors for tightness. | Q
Check fire smoke dampers for proper operation. | A
Inspect belts for proper tension and wear (if belts are replaced, record belt type and replacement date on unit) | A
Inspect entire motor and fan assembly, clean with a damp cloth. | A
Lubricate fan bearings and motors. | A
Lubricate all moving parts/connections, if necessary. | A
Operate dampers over the full modulation range, verify proper operation. | A
Preventive Maintenance Work Plan
Frequency Key
W – Weekly M - Monthly Q - Quarterly SA- Semi-Annually A- Annually SST - Seasonal Start-Up SSH - Season Shut Down
Other recommended tasks
Inspect all gauges and meters, ensure they are functional, replace if necessary. | A
Inspect coil fittings, tighten if necessary. | A
Utilize fin comb to straighten coil fins. | A
Clean/flush water or y-strainers and drip leg. | A
Inspect steam traps | A
Inspect all fan wiring for deterioration. | A
Tighten all electrical contacts. | A
Inspect motor starter/control center. | A
Verify operation of starter and inspect contact surfaces for pitting or wear. | A
Check damper linkage, set screws and blade adjustment for proper tightness. | A
Inspect bearing collar set screws on fan shaft, ensure tightness. | A
Inspect fan and motor sheaves for proper alignment. | A
Preventive Maintenance Work Plan
Frequency Key
W – Weekly M - Monthly Q - Quarterly SA- Semi-Annually A- Annually SST - Seasonal Start-Up SSH - Season Shut Down
Unit Heaters
Critical Tasks, to be performed semi-annually | Frequency | Status | Date Completed | Initials
Inspect unit for unusual noise and/or vibration, ensure that it is in good working order. | SA
If unit is not running or an identified problem requires the unit to be serviced, perform ALL Non- Critical Tasks listed below. | SA
Clean and re-install permanent filters or replace disposable filters. | SA
Provide lubrication, if necessary. | SA
Clean coils by vacuuming or brushing. | SA
Clean entire unit, motor and fan assembly with damp cloth. | SA
Other recommended tasks
Use fin comb to straighten coil fins. | A
Clean and flush strainers. | A
Preventive Maintenance Work Plan
Frequency Key
W – Weekly M - Monthly Q - Quarterly SA- Semi-Annually A- Annually SST - Seasonal Start-Up SSH - Season Shut Down
Pumps
Critical Tasks | Frequency | Status | Date Completed | Initials
Inspect unit for unusual noise and/or vibration, ensure that it is in good working order. | Q
Provide lubrication, if necessary. | Q
If unit is not running or an identified problem requires the unit to be serviced, perform ALL Non- Critical Tasks listed below. | Q
Flush and clean strainers. | Q
Check operation of gauges and record pressures and temperatures. | Q
Inspect seals and packing, tighten or replace as necessary. | Q
Lubricate impeller shaft bearings. | Q
Inspect motor and pump alignment. | Q
Other recommended tasks
Inspect mounting bolts and vibration isolators of the pump under load conditions. | A
Start and stop pump, noting any vibration and overall performance. | A
Inspect drive shaft coupling. | A
Preventive Maintenance Work Plan
Frequency Key
W – Weekly M - Monthly Q - Quarterly SA- Semi-Annually A- Annually SST - Seasonal Start-Up SSH - Season Shut Down
Heat Exchanger
Critical Tasks | Frequency | Status | Date Completed | Initials
Observe unit in operation, note any unusual noises and/or vibrations. | M
Inspect for leaks and/or corrosion. | M
Ensure that temperatures are within proper parameters. | M
Verify and calibrate all associated controls under load, verify proper sequences of | A
operation.
Inspect gauges and verify proper operation. | A
Inspect all safety devices for proper operation (vacuum breakers, hi-temperature safeties, relief valves, etc). | A
Inspect condensate drain system and clean as necessary. | A
Inspect steam traps for proper operation. | A
Check inlet and outlet water temperatures to measure performance of heat exchanger. Overhaul if necessary. | A
Visually inspect shell and tubes for fouling and/or corrosion. Assess tube condition. | If Necessary
Remove vessel hand-hole covers and inspect for any abnormal conditions (i.e. - scale, corrosion, etc.) | If Necessary
Clean shell and tubes chemically, if required/necessary. | If Necessary
*Non-destructive testing should be performed on the heat exchangers every three years.
Preventive Maintenance Work Plan
Frequency Key
W – Weekly M - Monthly Q - Quarterly SA- Semi-Annually A- Annually SST - Seasonal Start-Up SSH - Season Shut Down
Cabinet Unit Heaters
Critical Tasks, to be performed semi-annually | Frequency | Status | Date Completed | Initials
Inspect unit for unusual noise and/or vibration, ensure that it is in good working order. | SA
If unit is not running or an identified problem requires the unit to be serviced, perform ALL Non- Critical Tasks listed below. | SA
Clean and re-install permanent filters or replace disposable filters. | SA
Provide lubrication, if necessary. | SA
Clean coils by vacuuming or brushing. | SA
Clean entire unit, motor and fan assembly with damp cloth. | SA
Other recommended tasks
Use fin comb to straighten coil fins. | A
Clean and flush strainers. | A
Preventive Maintenance Work Plan
Frequency Key
W – Weekly M - Monthly Q - Quarterly SA- Semi-Annually A- Annually SST - Seasonal Start-Up SSH - Season Shut Down
Unit Ventilators
Critical Tasks, to be performed semi-annually | Frequency | Status | Date Completed | Initials
Inspect unit for unusual noise and/or vibration, ensure that it is in good working order. | SA
If unit is not running or an identified problem requires the unit to be serviced, perform ALL Non- Critical Tasks listed below. | SA
Clean and re-install permanent filters or replace disposable filters. | SA
Provide lubrication, if necessary. | SA
Clean coils by vacuuming or brushing. | SA
Clean entire unit, motor and fan assembly with damp cloth. | SA
Other recommended tasks
Clean condensate drip pan. | A
Flush condensate drain piping and eliminate potential blockages. | A
Use fin comb to straighten coil fins. | A
Clean and flush strainers. | A
Ensure proper operation of outside air damper and associated linkages. | A
Preventive Maintenance Work Plan
Frequency Key
W – Weekly M - Monthly Q - Quarterly SA- Semi-Annually A- Annually SST - Seasonal Start-Up SSH - Season Shut Down
Packaged Units
Critical Tasks, to be performed monthly | Frequency | Status | Date Completed | Initials
Check with operating or area personnel for deficiencies. | Q
Check unit for proper operation, excessive noise, or vibration. | Q
Clean intake side of condenser coils, fans, and intake screens. | Q
Check electrical wiring and connections; tighten loose connections. | A
Inspect fan(s) for bent blades or unbalance; adjust and clean as necessary. | A
Check belts for condition, proper tension and misalignment; adjust as required. | Q
Lubricate shaft bearings and motor bearings. | Q
Inspect piping and valves for leaks; tighten connections as necessary. | Q
Replace air filters. | Q
Check refrigerant pressure; add refrigerant as necessary. | Q
Clean evaporator drain pan, and drain piping as required. | A
Cycle the reverse cycle valve to insure proper operation. | Q
Clean area around equipment. | Q
Fill out maintenance checklist and report deficiencies. | Q
Preventive Maintenance Work Plan
Frequency Key
W – Weekly M - Monthly Q - Quarterly SA- Semi-Annually A- Annually SST - Seasonal Start-Up SSH - Season Shut Down
Steam Powered Domestic Hot Water Heater
Critical Tasks, to be performed weekly | Frequency | Status | Date Completed | Initials
Visually inspect all piping and valves, check for leaks. | W
Ensure that controls maintain setpoint. | W
Check insulation on heater, repair as necessary. | W
Check operation and condition of pressure relief valve. | SA
With unit under load, inspect for leaks and any signs of abnormal operation. | SA
Drain unit until all sediment and discolored water is expelled. | SA
Inspect tank exterior, fittings and hand-holes for signs of corrosion. | SA
Ensure that mixing valves operate as intended. | SA
Operate and inspect all control linkages. Adjust and lubricate linkages as necessary. | SA
Clean, test and inspect sight glasses, valves, fittings, drains and controls. | SA
Check steam control valves and steam traps for proper operation. | SA
Check electrical wiring connections on controls and switches. | SA
Exercise all manual isolation valves, as applicable, over full range and ensure full closure. | SA
Preventive Maintenance Work Plan
Frequency Key
W – Weekly M - Monthly Q - Quarterly SA- Semi-Annually A- Annually SST - Seasonal Start-Up SSH - Season Shut Down
Pressure Reducing Valves
Critical Tasks | Frequency | Status | Date Completed | Initials
Operate the controls over the full range of modulation to ensure proper operation of the valve and actuator. | A
Stroke the valve to ensure it maintains pressure setpoint. | A
Verify that the control valve is providing tight shutoff of the controlled medium. | A
Inspect condition of valve actuator. | A
Check for leaks. | A
Inspect pilot positioner. | A
Check/inspect pipe condition immediately after PRV station. | A
*Non-destructive testing should be performed on the high pressure steam piping every two years.
Preventive Maintenance Work Plan
Frequency Key
W – Weekly M - Monthly Q - Quarterly SA- Semi-Annually A- Annually SST - Seasonal Start-Up SSH - Season Shut Down
Split System Air Conditioners
Critical Tasks | Frequency | Status | Date Completed | Initials
Inspect all wiring for deterioration and tighten electrical contacts. Check for corrosion and cleanliness. | M
Observe unit in operation, note any unusual noise or vibration. | M
Observe unit in operation, note any unusual noise or vibration. | M
Inspect and clean condenser coils. Remove accumulated dirt and debris. | M
Check operation of head pressure controls | M
Lubricate motor and fan bearings | M
Observe unit in operation, note any unusual noise or vibration. | M
Inspect and replace filters if necessary. Write installation date on the filter. | M
Lubricate fan and motor bearings. | M
Other recommended tasks
Check control sequencing | A
Inspect mounting bolts and tighten if needed. | A
Verify unit is properly grounded. | A
Verify proper operation of crankcase heater (if applicable). | A
Check for refrigerant leaks and repair as necessary. | A
Check refrigerant levels and recharge if needed. | A
Check for oil leaks and repair as necessary. | A
Check compressor oil level (excludes hermetically sealed units), if unit is equipped with a sight glass. | A
Run machine, check action of controls, relays, switches and safeties or limit switches. | A
Verify unit operates at the proper suction and discharge pressures. Measure and record each. | A
Verify unit operates at proper discharge temperature. Measure and record temperature difference across the coil. | A
Air Cooled Condenser
Preventive Maintenance Work Plan
Frequency Key
W – Weekly M - Monthly Q - Quarterly SA- Semi-Annually A- Annually SST - Seasonal Start-Up SSH - Season Shut Down
Inspect all wiring for deterioration and tighten electrical contacts. Inspect for cleanliness and corrosion. | A
Check for arcing on contact. | A
Inspect condenser fans, bearings, housings, protective shields, motors, drives and/or belts. | A
Lubricate fan and motor bearings. | A
Inspect fan and motor starters. | A
Visually inspect motor starter/control/relay center. | A
Verify operation of starter and inspect contact surfaces for pitting or wear. | A
Inspect mounting bolts and tighten if needed. | A
Vacuum unit and surrounding area. | A
Clean (pressure wash) and comb condenser coils with a fin comb, if necessary. | A
Air Handling Unit (Evaporator)
Inspect bearing collar set screws on fan shaft to make sure they are tight. | A
Inspect blades and moving parts for cracks and excessive wear. | A
Inspect fan for vibration or excessive noise. | A
Inspect all wiring for deterioration and tighten electrical contacts. | A
Visually inspect motor starter for broken parts, contact arcing or any evidence of overheating. | A
Inspect dampers and fan blades for dust buildup and clean if necessary. | A
Vacuum unit and surrounding area. | A
Preventive Maintenance Work Plan
Frequency Key
W – Weekly M - Monthly Q - Quarterly SA- Semi-Annually A- Annually SST - Seasonal Start-Up SSH - Season Shut Down
Window Air Conditioning Units
Critical Tasks, to be performed monthly | Frequency | Status | Date Completed | Initials
Inspect unit for proper operation. | M
Clean coils and fins, straighten with a fin comb. | M
Clean or change filter. | M
Preventive Maintenance Work Plan
Frequency Key
W – Weekly M - Monthly Q - Quarterly SA- Semi-Annually A- Annually SST - Seasonal Start-Up SSH - Season Shut Down
Air Compressors
Critical Tasks | Frequency | Status | Date Completed | Initials
Drain receiver tank and check traps for proper operation. | SA
Change oil, resume operation and check oil for proper oil level and pressure. | SA
Change oil filter. After replacement, check for leaks. | SA
Change air intake filters. | SA
Check operation of the cut-in and cut-out pressure controls. | SA
Clean and degrease the compressor cooling fins. | SA
Other recommended tasks
Check and adjust belt tension. | SA
Check belt condition. Replace worn belts with matching sets. | SA
Check sheave alignment and level of shafts. | SA
Check operation of unloader and check valves. | SA
Check high pressure safety relief valve. | SA
Record compressor run times. | SA
Check operation of all safety relief valves. | SA
Inspect coalescent filters and change. | SA
Record pressure reducing valve settings and adjust as required. | SA
Check operation of all valve assemblies as required. | SA
Ensure that lead/lag/sequencing controls are operating compressors efficiently. | SA
Preventive Maintenance Work Plan
Frequency Key
W – Weekly M - Monthly Q - Quarterly SA- Semi-Annually A- Annually SST - Seasonal Start-Up SSH - Season Shut Down
Air Dryers
Critical Tasks | Frequency | Status | Date Completed | Initials
Check and record refrigerant pressures and temperatures. | SA
Clean condenser grills, if necessary. | SA
Operate drain trap and bypass valve. | SA
Preventive Maintenance Work Plan
Frequency Key
W – Weekly M - Monthly Q - Quarterly SA- Semi-Annually A- Annually SST - Seasonal Start-Up SSH - Season Shut Down
Expansion Tanks
Critical Tasks | Frequency | Status | Date Completed | Initials
Inspect tanks for signs of leakage or corrosion. | A
Verify proper tank level as noted in sight glass. | A
Preventive Maintenance Work Plan
Frequency Key
W – Weekly M - Monthly Q - Quarterly SA- Semi-Annually A- Annually SST - Seasonal Start-Up SSH - Season Shut Down
Absorption Chillers
Critical Tasks | Frequency | Status | Date Completed | Initials
Check with operating personnel for deficiencies; check operating log sheets for indications of increased temperature trends. | Q
Check unit for proper operation, excessive noise or vibration. | Q
Check pulley alignment and belts for condition, proper tension and misalignment on external purge pump system, if applicable; adjust for proper tension and or alignment. | Q
Check purge pump vacuum oil level, as required; add/change oil as necessary. | Q
Lubricate pump shaft bearings and motor bearings. | Q
Inspect cooling and system water piping circuits for leakage. | Q
Clean area around equipment. | Q
Fill out maintenance checklist and report deficiencies | Q
Check and clean strainers in all lines as required. | A
Check and service system controls, wirings and connections; tighten loose connections. | A
Preventive Maintenance Work Plan
Frequency Key
W – Weekly M - Monthly Q - Quarterly SA- Semi-Annually A- Annually SST - Seasonal Start-Up SSH - Season Shut Down
Centrifugal Water Cooled Chillers
Critical Tasks | Frequency | Status | Date Completed | Initials
Fill condenser and chilled water system. | SST
Ensure that unit's internal heater is operating properly before start-up. | SST
Inspect for proper operation of oil cooler. | SST
Ensure that both chilled and condenser water make-up systems are operating properly. | SST
Ensure proper operation of vanes and associated linkages. | SST
Check motor assembly for proper alignment and lubrication. | SST
Check operation of the lubrication system. | SST
Inspect for refrigerant/oil leaks. Repair leaks if found. | SST
Check refrigerant levels and recharge if needed | SST
Note unit run time, number of starts. | SST
Check all relays and operating/safety controls. | SST
Ensure that controls are providing proper/efficient operation of chiller. Check chilled water reset. | SST
While chiller is operating, document all pressures and temperatures. | SST
Observe all valves and piping, inspect for leaks, repair if necessary. | SST
Inspect that all actuators, linkages, moving parts associated with chiller system control are properly adjusted, tighten if necessary. | SST
Observe chiller components (i.e. - pumps, controls, motors, etc.) for proper operation. | SST
After first day of operation, flush and drain system to remove dirt and debris. | SST
Observe unit while in operation, note any unusual noise or vibration. | M
Inspect for refrigerant/oil leaks. Repair leaks if found. | M
Observe all valves and piping, inspect for leaks, repair if necessary. | M
While chiller is operating, document all pressures and temperatures. | M
Check refrigerant levels and recharge if needed | M
Flush/clean chilled and condenser water piping strainers. | M
Inspect lubrication system for proper operation. | M
Preventive Maintenance Work Plan
Frequency Key
W – Weekly M - Monthly Q - Quarterly SA- Semi-Annually A- Annually SST - Seasonal Start-Up SSH - Season Shut Down
Record run times and starts per chiller. | M
Inspect for refrigerant and oil leaks. All leaks to be repaired. | SSH
Check refrigerant levels and recharge if needed. | SSH
Flush/clean chilled and condenser water piping strainers. | SSH
Record run times and starts per chiller. | SSH
Ensure proper operation of freeze protection safety devices. | SSH
Take precautionary measures to prevent damage to system from freezing during winter months (i.e. - drain piping, utilize glycol). | SSH
Collect a sample of refrigerant/oil and submit to a qualified laboratory for analysis. | SSH
Blowdown pneumatic control lines and prepare for winter lay-up. | SSH
Clean and vacuum all electrical and control enclosures. | W
Perform meg test on chiller compressor motor and all other associated motors in the chilled/condenser water system. Compare to past readings. | W
Inspect for refrigerant and oil leaks. All leaks to be repaired. | W
Check refrigerant levels and recharge if needed. | W
With chiller locked/tagged out, inspect and adjust the guide vane linkage and operation. | W
Lubricate all control linkages and moving parts associated with the chiller. | W
Change compressor oil as specified by manufacturer. | W
Replace main oil filter. | W
Replace refrigerant filter/drier. | W
Check operation of starter and inspect contact surfaces for wear or pitting. | W
Check overload settings and check/tighten ALL electrical connections. | W
Solid state starters/VFD's must be serviced and maintained according to unit manufacturer's recommendations. | W
Inspect all relief valves for lubrication, condenser and evaporator sides. Disconnect piping inspect valve body. | W
Check and calibrate all temperature sensors utilized for chiller operation (i.e., chilled water, condenser water, refrigerant, oil), if possible. | W
Check and calibrate all differential pressure and flow switches utilized | W
for chiller operation.
Preventive Maintenance Work Plan
Frequency Key
W – Weekly M - Monthly Q - Quarterly SA- Semi-Annually A- Annually SST - Seasonal Start-Up SSH - Season Shut Down
Check all pressure transducers against a pressure gage. Recalibrate if needed. | W
Inspect, clean and service refrigerant float system. | W
Clean evaporator tubes every three years. | W
Clean condenser tubes every three years. | W
Perform eddy current testing every three years on both the evaporator and condenser | W
tubes.
Preventive Maintenance Work Plan
Frequency Key
W – Weekly M - Monthly Q - Quarterly SA- Semi-Annually A- Annually SST - Seasonal Start-Up SSH - Season Shut Down
Reciprocating Air Cooled Chillers
Critical Tasks | Frequency | Status | Date Completed | Initials
Check unit for proper operation, excessive noise or vibration. | M
Run system diagnostics test. | M
Check oil level in sight glass of lead compressor only, add oil as necessary. | M
Check superheat and subcooling temperatures. | A
Check liquid in line sight glass, oil and refrigerant pressures. | M
Check contactors, sensors and mechanical safety limits. | A
Check electrical wiring and connections; tighten loose connections. | A
Clean intake side of condenser coils, fans, and intake screens. | A
Inspect fan(s) or blower(s) for bent blades or imbalance. | A
Lubricate shaft bearings and motor bearings as required. | A
Inspect plumbing and valves for leaks, adjust as necessary. | M
Check evaporator and condenser for corrosion. | M
Clean chiller and surrounding area. | M
Fill out maintenance checklist and report deficiencies. | M
Preventive Maintenance Work Plan
Frequency Key
W – Weekly M - Monthly Q - Quarterly SA- Semi-Annually A- Annually SST - Seasonal Start-Up SSH - Season Shut Down
Cooling Towers
Critical Tasks, to be performed during seasonal start-up | Frequency | Status | Date Completed | Initials
Clean cooling towers by flushing, blowing down all associated piping. | SST
Inspect sprayer heads. | SST
Inspect structural supports. | SST
Inspect and clean louvers. | SST
Inspect collection trays and suction screens for plugging and clean. | SST
Inspect and clean drift eliminators. | SST
Test motor winding continuity on condenser fan motors. | SST
Inspect fans, bearings, housings, protective shields, motors, drives and/or belts. Lubricate as necessary. Record observations. | SST
Inspect fan motor starters. | SST
Visually inspect motor starter/control center. | SST
Check operation of starter and inspect contact surfaces for wear or pitting. | SST
Check overload settings and check/tighten ALL electrical connections. | SST
Vacuum cabinets to eliminate dust build-up. | SST
Operate gear reducer (where applicable) until oil is warm. Drain oil and refill with new. | SST
Start unit(s) and operate. If applicable, sequence unit(s) through entire operating range. | SST
Record and address any abnormal vibrations. | SST
Observe cooling tower to ensure proper operation. Inspect for unusual noise or vibration. | M
Inspect and clean louvers, if required. | M
Check operation of make-up water valve and any associated controls/linkages, lubricate if necessary. | M
Visually check fan gear reducer/drive oil sample for presence of water and/or sludge. | M
Check oil level in gear reducer/drive (if applicable). Add if required and record amount. | M
Provide Water Treatment. | M
During winter months ensure proper operation of basin heaters, if present. | M
Preventive Maintenance Work Plan
Frequency Key
W – Weekly M - Monthly Q - Quarterly SA- Semi-Annually A- Annually SST - Seasonal Start-Up SSH - Season Shut Down
Verify that alternating/lead/lag controls are operating the towers properly. | M
Clean/Flush condenser water strainers/sand filters. | M
Drain condenser water from cooling towers and any piping that could freeze during the winter. | SSH
Secure all makeup water systems. | SSH
Inspect condition of spray nozzles and fill, check all structural supports and bolted connections and tighten as required. | SSH
Visually inspect the drift eliminators. Remove debris or scale as required. | SSH
Record and address any abnormal vibrations. | SSH
Preventive Maintenance Work Plan
Frequency Key
W – Weekly M - Monthly Q - Quarterly SA- Semi-Annually A- Annually SST - Seasonal Start-Up SSH - Season Shut Down
Gas Fired Domestic Hot Water Heater
Critical Tasks | Frequency | Status | Date Completed | Initials
Visually inspect all piping and valves, check for leaks. | W
Ensure that controls maintain set point. | W
Check insulation on heater, repair as necessary. | W
Drain unit until all sediment and discolored water is expelled. | SA
With unit under load, inspect for leaks and any signs of abnormal operation. | SA
Inspect tank exterior, fittings and hand-holes for signs of corrosion. | SA
Ensure that mixing valves operate as intended. | SA
Operate and inspect all control linkages. Adjust and lubricate linkages as necessary. | SA
Inspect and clean combustion air passages. | SA
Test operation of gas pressure regulator and adjust setting if necessary. | SA
Clean, test and inspect sight glasses, valves, fittings, drains and controls. | SA
Inspect ignition and pilot assembly. Clean and adjust igniter if necessary. | SA
Exercise all manual isolation valves, as applicable, over full range and ensure full closure. | SA
Preventive Maintenance Work Plan
Frequency Key
W – Weekly M - Monthly Q - Quarterly SA- Semi-Annually A- Annually SST - Seasonal Start-Up SSH - Season Shut Down
Vacuum Pump Units
Critical Tasks, to be performed semi-annually | Frequency | Status | Date Completed | Initials
Inspect operation of vacuum pump for excessive vibration, noise, heat, etc. | SA
Change oil, resume operation and check oil for proper oil level and pressure. | SA
Change oil filter. After replacement, check for leaks. | SA
Change air intake filters. | SA
Check operation of the cut-in and cut-out pressure controls. | SA
Other recommended tasks
Check belt condition. Replace worn belts with matching sets. Check and adjust belt | SA
tension.
Check sheave alignment and level of shafts. | SA
Check operation of unloader and check valves. | SA
Record vacuum run times. | SA
Check high pressure safety relief valve. | SA
Check operation of motor operation and starter. Record motor amperage and voltage readings per phase. | SA
Check operation of all safety relief valves. | SA
Check operation of all valve assemblies as required. | SA
Clean and degrease the compressor cooling fins. | SA
Preventive Maintenance Work Plan
Frequency Key
W – Weekly M - Monthly Q - Quarterly SA- Semi-Annually A- Annually SST - Seasonal Start-Up SSH - Season Shut Down
Steam Boilers
Critical Tasks | Frequency | Status | Date Completed | Initials
Annual tasks should be performed at the end of each heating season and coordinated with annual boiler inspections. | A
Boiler Shell | A
Remove the rear and/or side access panel and cleanout. | A
Access the fireside of the boiler and thoroughly clean all internal surfaces, vacuum surfaces and remove all debris. | A
Clean spaces leading from exhaust breeching to exhaust flue. Inspect for corrosion or damage. | A
Inspect and replace, as necessary, all gaskets. | A
Peripherals | A
Inspect burner natural gas valves, oil valves, air intake damper and back draft damper linkages, adjust if necessary. | A
Lubricate all burners, damper actuator linkage moving parts and pivot points. | A
Exercise joints and remove excess lubricant. | A
Inspect all fuel solenoid valves for unusual noises, full closure and proper operation. | A
Check fuel cam profile spring for wear, scoring, discoloration. | A
Clean and inspect all fuel oil strainers. | A
Check oil pressure gauge for accuracy. | A
Check actuator motor for proper operation. | A
Check ignition electrode/pilot for proper gap/flame, adjust if necessary. | A
Check/test burner control panel/system for the following indicating lights/safety devices/alarms; flame failure, high/low gas/oil pressure, air switch. | A
Inspect flame detector lens, clean if necessary. | A
For electric ignition systems, test and record voltage readings on each side of the ignition transformer. | A
Inspect combustion fan motor and ensure that fan is secured tightly to shaft. Provide lubrication and clean fan blades. If fan is belt driven, check for proper alignment. | A
Preventive Maintenance Work Plan
Frequency Key
W – Weekly M - Monthly Q - Quarterly SA- Semi-Annually A- Annually SST - Seasonal Start-Up SSH - Season Shut Down
Check low/high water limit controllers, adjust/tighten linkages if necessary. If probe type, ensure that sensors are clean and free of debris. | A
Inspect boiler safety relief valve and assure proper operation. | A
Ensure proper operation of low/high temperature limit controllers. | A
Tune boiler for operation on the primary fuel. A combustion gas analyzer should be used to check burner efficiency at 25%, 50%, 75% and 100% firing rate. | A
Other observations should be made during boiler tune-up such as fuel/air ratio, flame color/spread, opacity, stack temperatures and O2/Nox/CO/CO2 concentrations. | A
Record all observations | A
Ensure that boiler components are operating in proper sequence. | W
Visually inspect all control linkages and components for proper operation, lubricate moving parts, if necessary. | W
Inspect boiler piping, valves and fitting for leaks. | W
Ensure that boiler pressuretrol set points are not excessively high. | W
Experiment with lowering set points in order to conserve energy while meeting building demand. | W
If problems or inefficient operation are identified correct deficiencies immediately. | W
*Non-destructive testing should be performed on the boilers every three years.
Preventive Maintenance Work Plan
Frequency Key
W – Weekly M - Monthly Q - Quarterly SA- Semi-Annually A- Annually SST - Seasonal Start-Up SSH - Season Shut Down
Water Boilers
Critical Tasks | Frequency | Status | Date Completed | Initials
Annual tasks should be performed at the end of each heating season and coordinated with annual boiler inspections. | A
Boiler Shell | A
Remove the rear and/or side access panel and cleanout. | A
Access the fireside of the boiler and thoroughly clean all internal surfaces, vacuum surfaces and remove all debris. | A
Clean spaces leading from exhaust breeching to exhaust flue. Inspect for corrosion or damage. | A
Inspect and replace, as necessary, all gaskets. | A
Peripherals | A
Inspect burner natural gas valves, oil valves, air intake damper and back draft damper linkages, adjust if necessary. | A
Lubricate all burners, damper actuator linkage moving parts and pivot points. | A
Exercise joints and remove excess lubricant. | A
Inspect all fuel solenoid valves for unusual noises, full closure and proper operation. | A
Check fuel cam profile spring for wear, scoring, discoloration. | A
Clean and inspect all fuel oil strainers. | A
Check oil pressure gauge for accuracy. | A
Check actuator motor for proper operation. | A
Check ignition electrode/pilot for proper gap/flame, adjust if necessary. | A
Check/test burner control panel/system for the following indicating lights/safety devices/alarms; flame failure, high/low gas/oil pressure, air switch. | A
Inspect flame detector lens, clean if necessary. | A
For electric ignition systems, test and record voltage readings on each side of the ignition transformer. | A
Inspect combustion fan motor and ensure that fan is secured tightly to shaft. Provide lubrication and clean fan blades. If fan is belt driven, check for proper alignment. | A
Preventive Maintenance Work Plan
Frequency Key
W – Weekly M - Monthly Q - Quarterly SA- Semi-Annually A- Annually SST - Seasonal Start-Up SSH - Season Shut Down
Check low/high water limit controllers, adjust/tighten linkages if necessary. If probe type, ensure that sensors are clean and free of debris. | A
Inspect boiler safety relief valve and assure proper operation. | A
Ensure proper operation of low/high temperature limit controllers. | A
Tune boiler for operation on the primary fuel. A combustion gas analyzer should be used to check burner efficiency at 25%, 50%, 75% and 100% firing rate. | A
Other observations should be made during boiler tune-up such as fuel/air ratio, flame color/spread, opacity, stack temperatures and O2/Nox/CO/CO2 concentrations. | A
Record all observations | A
Ensure that boiler components are operating in proper sequence. | W
Visually inspect all control linkages and components for proper operation, lubricate moving parts, if necessary. | W
Inspect boiler piping, valves and fitting for leaks. | W
Ensure that boiler temperature set points are not excessively high. | W
Experiment with lowering set points in order to conserve energy while meeting building demand. | W
If problems or inefficient operation are identified correct deficiencies immediately. | W
*Non-destructive testing should be performed on the boilers every three years.
Preventive Maintenance Work Plan
Frequency Key
W – Weekly M - Monthly Q - Quarterly SA- Semi-Annually A- Annually SST - Seasonal Start-Up SSH - Season Shut Down
Submersible Pumps (Sump/Ejector)
Critical Tasks | Frequency | Status | Date Completed | Initials
Check electrical cords, plugs and connections. | SA
Activate float switches and check pumps for proper operation. | SA
Lubricate pumps as required. | SA
Inspect packing and tighten as required. | SA
Check pumps for misalignment and bearings for overheating | SA
Clean out trash from sump bottom. | SA
Preventive Maintenance Work Plan
Frequency Key
W – Weekly M - Monthly Q - Quarterly SA- Semi-Annually A- Annually SST - Seasonal Start-Up SSH - Season Shut Down
Steam Radiators
Critical Tasks | Frequency | Status | Date Completed | Initials
Remove radiator valve; Install radiator valve | A
Observe radiator and ensure proper operation. Tasks to be performed during heating season only. | M
Preventive Maintenance Work Plan Frequency Key W – Weekly M - Monthly Q - Quarterly SA- Semi-Annually A- Annually SST - Seasonal Start-Up SSH - Season Shut Down Steam Traps
Critical Tasks | Frequency | Status | Date Completed | Initials
Observe trap, and ensure proper operation. Repair/replace as necessary. Tasks to be performed during heating season only. | A
*Non-destructive testing should be performed on the steam traps every year.
Preventive Maintenance Work Plan
Frequency Key
W – Weekly M - Monthly Q - Quarterly SA- Semi-Annually A- Annually SST - Seasonal Start-Up SSH - Season Shut Down
Emergency Diesel Generator
Critical Tasks | Frequency | Status | Date Completed | Initials
Check with the operating or area personnel for any obvious deficiencies. | M
Check turbine oil level; add oil as required. | M
Change turbine oil and oil filter; check transmission oil level. | M
Check that the crankcase heater is operating properly. | M
Replace turbine air filter. | M
Check wiring, connections, switches, etc; adjust as required. | M
Check starter for proper operation; lubricate as necessary. | M
Check fuel nozzles, fuel regulator and ignition device condition; service or replace as required | M
Perform 30 minute generator test run; check for proper operation. | M
Check and record transmission oil pressure and temperature, and natural gas pressure | M
Record running time | M
Check that the charger is operating properly | M
Check for any signs of corrosion on battery terminals or wires | M
Check the electrolyte level in the batteries; add if required. | M
Check the specific gravity of the electrolyte in a 10% sample of the batteries | A
Check 25% of terminal to-cell connection resistance; rehabilitate connections as required; add anti-corrosion grease to battery terminals and connections. | A
Measure and record individual cell and string float voltages | A
Clean area around generator. | M
Fill out maintenance checklist and report deficiencies. | M